# Metering Installation Error Report

# (Data source: explore_1.xlsx. Error calculated: Fri Mar 13 13:54:59 2020.)

The error calculated for the given load profile is +0.26 %.

The expanded uncertainty at an estimated 95% level of confidence is 0.16 %.

The uncertainty interval extends from +0.10 % to +0.42 %.

## Installation error over the phase and current ranges that match the load profile.

## Annual load profile used for this error calculation.

## Component calibration data with calculated fits over the calibration ranges.

### Current Transformer.

### Voltage Transformer.

### Meter.

# Additional Information

## Uncertainty Contribution Summary

Uncertainty contribution by component as a percentage of total variance, Meter:  19  %, CT:  45  %, VT:  36  %.

## Text Output From Calculation Process

Meter data

Fit has lower uncertainty than expected from calibration data, so type B component added.

CT ratio data

Fit has lower uncertainty than expected from calibration data, so type B component added.

CT phase data

Good fit.

VT ratio data

Fit has lower uncertainty than expected from calibration data, so type B component added.

VT phase data

Fit has lower uncertainty than expected from calibration data, so type B component added.

Max current = 50.59 %, Min current = 5.75 %, Max phase = 86.03  degrees, Min phase = -48.98  degrees

Budget for overall error by coefficients

0.260, u=0.079, df=120.3

a2 CT_e: 0.0663702

a0 VT_e: 0.0515479

a1 VT_e: 0.05104

a0 CT_e: 0.0418284

Meter temperature coefficient: 0.0357071

Meter harmonic dependence: 0.0282843

Site harmonics: 0.0282843

Site voltage: 0.0226716

Meter voltage dependence: 0.0212132

b0 meter: 0.0202546

a2 CT_p: 0.0185814

b0 CT_e: 0.0183737

a1 CT_e: 0.0163646

b0 VT_e: 0.0163636

CT calibration burden: 0.0155754

Site CT burden: 0.0155754

a0 VT_p: 0.0144399

a1 VT_p: 0.0142976

Meter frequency dependence: 0.0132583

Site frequency: 0.0124713

a0 CT_p: 0.0117172

a0 meter: 0.00824024

Site temperature: 0.00798931

VT calibration burden: 0.00796915

Site VT burden: 0.00796915

a1 CT_p: 0.00458842

b0 VT_p: 0.00439312

a2 meter: 0.00424807

a3 meter: 0.00416099

a1 meter: 0.00266613

CT temperature coefficient of phase: 0.000233859

VT temperature coefficient of phase: 0.000133258

CT calibration temperature: 6.07442E-05

VT calibration temperature: 3.10797E-05

VT temperature coefficient of error: 2.4479E-05

CT temperature coefficient of error: 2.12541E-05